| Checked by Supervisor / Initials & date |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Location: |  |  |  | SAM Details: |  |  |  |  |
| Company Name: |  |  |  | Date: Start time: Finish Time: |  |  |  |  |
| Staff name: |  |  |  | Staff name: |  |  |  |  |
| Team Leader (Print): |  |  |  | Signature: |  |  |  |  |
| Daily Completion |  |  |  |  |  |  |  |  |
| HDODF / Address | Work comp |  |  |  |  |  |  |  |
|  |  | Location |  |  |  |  |  |  |
| IN PROCESS INSPECTION FOR HDODF |  |  |  |  |  | Y | N | N/A |
| All external cables entering Telstra exchanges are secured to the cable trays on the opposite side as far away from existing Telstra cables as practicable & are to be secured at intervals of: (Horizontal ≤72F = 450mm • Horizontal ≥72F = 1000mm / Vertical = 1.5m) - All cable ties are cut flush. |  |  |  |  |  |  |  |  |
| External cables entering Telstra exchanges from chambers/manholes or floor level penetrations, have the fire - Stopping/proofing materials reinstalled. |  |  |  |  |  |  |  |  |
| External cables entering Telstra exchanges are labelled correctly and with correct naming convention. Must be are at least 1 meter above point of entry from cable chambers/manholes at change of floor level penetrations. Within 1M above the entry to the HDODF rack. |  |  |  |  |  |  |  |  |
| External cables entering or installed in exchanges are in the correct trays/ riser trays as per NDD and floor plans. |  |  |  |  |  |  |  |  |
| External cables (if) installed in horizontal trays are checked where possible to ensure: No intertwining or crossing of other cables and secured at regular intervals by cables ties. |  |  |  |  |  |  |  |  |
| External cables (if) installed in horizontal trays are checked from above to ensure that when changes of direction occur, the minimum bend radius is not exceeded and there are no signs of kinking. |  |  |  |  |  |  |  |  |
| Optic fibre cable secured on the ramp drop-off and to the comb above the HDODF with cable ties. |  |  |  |  |  |  |  |  |
| Cable is secured: (to comb just inside top of HDODF & • to top comb of base section & • all cables ties cut flush) |  |  |  |  |  |  |  |  |
| Strength Member (SM) is installed and tightly secured to the SM fixing bar. |  |  |  |  |  |  |  |  |
| Flexible conduit has the slit cut in rear of conduit to allow a neat installation up the cable and over the sheath and taped off (with no tubes exposed) |  |  |  |  |  |  |  |  |
| Cable installed, secured to the cable breakout, and routed to the CEMT tray with convoluted tubing correctly. |  |  |  |  |  |  |  |  |
| CEMT cables follow numbering plan and are installed crossed over other cables. |  |  |  |  |  |  |  |  |
| Cables installed and broken out correctly across CEMT. |  |  |  |  |  |  |  |  |
| HDODF rack labelled and correct naming convention followed. |  |  |  |  |  |  |  |  |
| HDODF installed in the correct location as per the NDD and floor Plan. |  |  |  |  |  |  |  |  |
| Tubes broken out into correct sub racks with coloured stickers on ODF sub racks in correct order (matching the colour of the tubes). |  |  |  |  |  |  |  |  |
| Fanning of transport tubes into the ODF sub racks is not exceeding the min bend radius limits & is not too excessive with the transport tube loops. |  |  |  |  |  |  |  |  |
| HDODF installed as per design and to standard. |  |  |  |  |  |  |  |  |
| DSS cables labelled and naming convention followed. |  |  |  |  |  |  |  |  |
| HDODF rack labelled and naming convention followed with sub rack label placed on the front left of the chassis. |  |  |  |  |  |  |  |  |
| Inter-rack cabling installed and labelled as per design. |  |  |  |  |  |  |  |  |
| Correct routing of incoming DSS cable within HDODF rack. |  |  |  |  |  |  |  |  |
| Ribbons lose tubes secured to CEMT and routed to ribbon breakout units with convoluted tubing correctly. |  |  |  |  |  |  |  |  |
| Ribbons run from breakout units via transport tubing to optical sub rack. |  |  |  |  |  |  |  |  |
| Sub-racks have correct range of fibres installed as per NBN Co design. |  |  |  |  |  |  |  |  |
| Correct type of sub-rack label fitted & Labelling convention followed. |  |  |  |  |  |  |  |  |
| Sub rack showing splice organiser tray has been labelled correctly. |  |  |  |  |  |  |  |  |
| Protection tubes are secured and fully housed in the clips and guides with Velcro. |  |  |  |  |  |  |  |  |
| There is no stress on the protection tube when sub-rack & splice trays are being opened/closed, near the entrance to the splice trays. |  |  |  |  |  |  |  |  |
| Splice tray stack is secure & have cover fitted. |  |  |  |  |  |  |  |  |
| Ribbon fibres laid clockwise on to splice tray to make a stored length of 1020 mm inside the splice case. |  |  |  |  |  |  |  |  |
| Splice protectors labelled. |  |  |  |  |  |  |  |  |
| Fibres do not exceed the minimum bend radius of 30mm. |  |  |  |  |  |  |  |  |
| Comments: |  |  |  |  |  |  |  |  |